## Checklist
Commercial Electrical Panel Safety Inspection
Electrical · Checklist · Free template from forz.io
Company:
Date:
Technician:
Panel & site identification
Item | Result (Pass / Fail / N/A) | Notes
Customer / facility
Account #
Building / floor
Site address
Room / area served
Panel designation as labeled (MDP, DP-1, LP-2…)
Manufacturer
Catalog / type #
Panel type: Service entrance / Main distribution / Panelboard / Load center / Switchboard / Motor control center
Enclosure NEMA rating
Voltage / phase / wire
Main bus rating (A)
Main breaker / MLO size
Circuit spaces / poles
SCCR / AIC marked
Rating: Series-rated / Fully-rated
Fed from (panel / transformer)
Feeder conductor size
Feeder OCPD
AHJ
NEC / NFPA 70B edition adopted
Inspection cycle: Monthly / Quarterly / Semiannual / Annual
Inspector name
License / qualified-person cert #
Last inspection date
Prior report # / open deficiencies
Pre-work safety & risk assessment
Item | Result (Pass / Fail / N/A) | Notes
Job briefing completed; energized-work risk assessment / energized electrical work permit reviewed where applicable
Arc-flash and shock boundaries identified; arc-rated PPE and voltage-rated gloves match the label or incident-energy analysis
Insulated tools and rated meter (CAT III / CAT IV) used; test instruments within calibration
Lockout / tagout applied and absence-of-voltage test performed before contact with conductors or removal of barriers
Scope defined: energized visual / IR survey vs. de-energized internal inspection and torque verification
Two-person rule / standby person in place for any work inside the shock-protection boundary
Connections & torque
Item | Result (Pass / Fail / N/A) | Notes
Main lugs / main breaker line and load terminations torqued to manufacturer's value; applied value recorded below
Neutral and equipment-ground bar terminations checked / torqued; one conductor per terminal unless listed for more
Feeder and branch breaker terminations checked / torqued with a calibrated torque tool
No stripped, skewed, or cross-threaded setscrews; over-tightened connections identified and corrected
Working clearance & access
Item | Result (Pass / Fail / N/A) | Notes
Working depth clear (commonly cited 36 in / 914 mm for 0–150 V to ground)
Working width clear (greater of 30 in / 762 mm or equipment width); doors and hinged panels open a full 90°
Headroom clear (commonly cited 6 ft 6 in / 2.0 m); no pipes, ductwork, or overhead obstructions
Dedicated equipment space above panel (commonly cited 6 ft or to structural ceiling) free of foreign piping, ducts, storage
No storage, materials, or fixtures encroaching on the working space; floor area clear
Illumination adequate at the working space; panel not relied on as sole light
At least one entrance of sufficient area to the working space; egress not blocked
Panel accessible without removing obstacles or passing through locked spaces controlled by others
Labeling, identification & arc-flash marking
Item | Result (Pass / Fail / N/A) | Notes
Arc-flash label present, legible, dated; shows nominal voltage plus incident energy (cal/cm²) and working distance OR PPE category (not both)
Arc-flash / shock-hazard marking matches latest study; study revision date recorded and not expired per facility policy
Available fault current and calculation date marked on equipment (where required)
Service-entrance marking and maximum available fault current label present on service equipment
Panel directory / circuit schedule complete, legible, and current; spare and unused circuits identified
Each overcurrent device clearly and durably identified as to purpose; no ambiguous handwriting
Disconnecting means clearly marked and the load it controls identified
Warning, restricted-access, and energized-equipment signage present, intact, and readable
Enclosure, bus & breaker condition
Item | Result (Pass / Fail / N/A) | Notes
Enclosure free of corrosion, rust, water intrusion, condensation, and pest entry; rated for the environment
Deadfront and all blank fillers in place; no open knockouts, missing twistouts, or exposed energized parts
Cover, hinges, latches, and locking provisions intact; door closes and seals properly
No signs of overheating (discoloration, melted insulation, charring, burnt odor) at breakers, bus, or terminals
Bus bars, breaker stabs, and connections free of pitting, arcing tracks, corrosion, and discoloration
Breakers seated firmly on bus; handles operate freely; no cracked cases or broken handles
Breakers exercised (off / on) where allowed, or noted as due per maintenance schedule
No double-tapped breakers, unlisted breaker / panel combinations, or improper brands used as fillers
Conductor insulation undamaged; no nicks, overheating, brittleness, or insulation pulled past the lug
Wire bending space and gutter fill within limits; conductors dressed and not strained at terminations
Panel not overcrowded; number of circuits within the panel's listed maximum
Grounding, bonding & protective devices
Item | Result (Pass / Fail / N/A) | Notes
Main bonding jumper present and intact; neutral-to-ground bond made at the service disconnect only
Subpanels: isolated (floating) neutral bar, no neutral-to-ground bond, no shared neutral / ground terminations
Grounding electrode conductor and equipment grounding conductors landed, sized, and free of corrosion or looseness
Bonding continuity to enclosure and metallic raceway confirmed; bonding bushings present where required
GFCI protection tested (test button / tester); trips and resets correctly
AFCI protection tested with test button; trips and resets correctly
Surge protective device (SPD), where installed, shows normal status; connections sound
Torque record
Item | Result (Pass / Fail / N/A) | Notes
Termination / location ¦ Mfr. value ¦ Applied value ¦ Unit ¦ Corrected ¦ Notes ¦ Init.
Infrared thermography
Item | Result (Pass / Fail / N/A) | Notes
IR survey performed under at least ~40% rated load with deadfront removed by a qualified thermographer
Each hot connection traced to lug, stab, breaker, splice, or bus and tagged for corrective action with priority
Load balancing reviewed where a phase shows heating from imbalance rather than a loose connection
IR baseline readings recorded for trending against prior and future inspections
Hot-spot severity by ΔT (commonly cited NETA guidance)
Item | Result (Pass / Fail / N/A) | Notes
1–3 °C : Investigate / trend
4–15 °C : Repair as scheduling permits
16–40 °C : Repair soon
>40 °C : Above ambient: immediate / imminent failure
Hot-spot log
Item | Result (Pass / Fail / N/A) | Notes
# ¦ Location / component (lug, stab, breaker, splice, bus) ¦ Measured ° ¦ Reference ° ¦ ΔT ¦ Severity ¦ Priority ¦ Image / tag #
Load readings
Item | Result (Pass / Fail / N/A) | Notes
Voltage L–L (V)
Voltage L–N (V)
Current (A)
Calculated demand vs. bus and main breaker rating (A)
Phase imbalance (%)
Continuous load vs. OCPD rating, commonly cited 80% limit (flag oversized / undersized OCPD) (%) · ≤ 80%
Ground resistance / continuity (if in scope) (Ω)
Power-quality observations (sag, flicker, harmonics) (n/a)
Results
Item | Result (Pass / Fail / N/A) | Notes
Overall result: Pass / Deficiencies noted / Critical safety hazard / Equipment removed from service
Immediate hazard flagged (exposed parts, blocked clearance, failed bond, imminent-failure hot spot): None / Yes: owner notified at once
Deficiencies & corrective action
Item | Result (Pass / Fail / N/A) | Notes
# ¦ Circuit / location ¦ Description ¦ Severity ¦ NEC / NFPA ref. ¦ Corrective action / priority ¦ WO / quote #
Owner / rep. notified (name)
Contact
Date notified
Photos / thermal images (count)
Reference #s
Next inspection due
Interim re-scan dates for monitored hot spots
Inspector signature · license / cert #
Owner / authorized representative signature
Summarized from NEC, NFPA 70B, NFPA 70E, and NETA thermography practice. Clearances, label content, fault-current marking, torque values, and severity bands depend on edition, manufacturer, and conditions; verify with your AHJ, the adopted edition, the arc-flash study, and manufacturer specifications. This form is a starting point and does not replace inspection, testing, and maintenance by qualified personnel.