## Checklist
HVAC Seasonal Preventive Maintenance Checklist
HVAC · Checklist · Free template from forz.io
Company:
Date:
Technician:
Equipment & site
Item | Result (Pass / Fail / N/A) | Notes
Customer / facility name
Account #
PMA / contract ref.
Site address
Building / suite
Unit ID / tag
Area / zone served
Units covered this visit
Equipment location: Rooftop / Mech. room / Closet / Pad
Equipment type: Split system / Packaged RTU / Heat pump / Mini-split / AHU + separate condensing unit
Heat source: Gas furnace / Electric strips / Heat pump / Dual fuel
Condensing unit make & model
Condensing unit serial #
AHU / furnace make & model
AHU / furnace serial #
Capacity (tons / BTU/h)
Voltage / phase
Rated FLA / RLA / MCA
Heat input (BTU/h or kW)
Refrigerant: R-410A / R-454B / R-32 / R-22 (legacy)
Filter size(s) & qty
Metering device: TXV / EEV / Fixed orifice / piston
Filter type: Pleated / Media / Washable
Belt size
Visit: Cooling tune-up / Heating tune-up
Arrival time
Departure time
Outdoor temp at start
Indoor temp at start
Technician
EPA 608 cert #
EPA 608 type: Type I / Type II / Type III / Universal
Prior visit ref. & open deficiencies
Runtime hours (if logged)
Filters, airflow & cabinet
Item | Result (Pass / Fail / N/A) | Notes
Return-air filter(s) inspected; replaced with correct size and MERV, arrow oriented to airflow
Filter rack, gaskets, and access panels seal with no air bypass
Supply registers, return grilles, and accessible ductwork clear; no crushed or disconnected flex
Cabinet panels, screws, and gaskets secure; no leakage at seams or wiring penetrations
Outdoor unit clearance on all sides and above; coil free of grass, leaves, lint, stored material
Pad or curb level, secure, no standing water; mounting hardware tight
Suction-line insulation intact; line-set supports and isolation grommets in place
Coils, condensate & drain
Item | Result (Pass / Fail / N/A) | Notes
Condenser coil inspected; cleaned with approved cleaner and rinsed; fin-comb work noted
Evaporator coil inspected for dirt, growth, frost, even airflow; cleaned where accessible
Fins combed where flattened; no oil residue indicating a leak at U-bends or return bends
Primary drain pan clean, draining, no cracks, rust-through, or standing water
Condensate line cleared and flushed; trap intact and primed; flow verified to termination
Auxiliary pan clean and dry; float (safety) switch present and tested to interrupt
Condensate pump cycles on float, drains fully, check valve holds; reservoir clean
Drain pan treatment tablet or strip installed (per agreement scope)
Blower wheel and housing inspected for dirt loading and imbalance; cleaned where fouled
Electrical, motors & controls
Item | Result (Pass / Fail / N/A) | Notes
Disconnect, breaker, and fuse sizing match nameplate MCA / max fuse; fuses and lugs tight
Line- and low-voltage connections tightened; no discoloration, melted insulation, or burnt smell
Contactor contacts checked for pitting, burning, chatter; coil pull-in confirmed; replaced if pitted
Run / start capacitors replaced if out of tolerance or bulged (record µF in readings)
Condenser fan motor bearings checked; motor cleaned and lubricated where serviceable
Indoor blower: ECM module or PSC capacitor and speed taps verified
Belt drive: belt checked for cracks, glazing, wear; tension and sheave alignment set; pulleys tight
Blower and condenser-fan bearings checked for noise and play; lubricated per mfr. where fitted
Crankcase heater operational (if equipped); low-ambient and head-pressure controls verified
Safety controls tested: high / low pressure switches, freeze stat, float switch, limit interlocks
Cooling season: refrigerant circuit
Item | Result (Pass / Fail / N/A) | Notes
Compressor discharge line checked for overheating; no signs of flooding or starving
Leak check performed (electronic, soap, or UV) at fittings, Schrader cores, and coil where suspected
Schrader caps and core seals verified; refrigerant added recorded by type and weight on EPA leak log
TXV / EEV sensing bulb secure and insulated; superheat response confirmed
Heating season: gas furnace & combustion safety
Item | Result (Pass / Fail / N/A) | Notes
Burner assembly, flame sensor, and igniter (hot-surface or spark) inspected and cleaned
Burner flames steady and blue; no lifting, rollout, or yellow tipping
Gas piping, valve, and unions leak-checked at all connections; no leaks
Heat exchanger inspected (visual / camera) for cracks, corrosion, rust scale, separation
Inducer motor, pressure switch, and condensate trap and tubing (high-efficiency) clear and operating
Flue / vent connector, draft, and combustion-air openings clear; pitch and clearance correct
CO alarms confirmed present
Limit switch, rollout switch, and gas-valve safety shutoff tested
Heat pump: heating mode & defrost
Item | Result (Pass / Fail / N/A) | Notes
Reversing valve shifts fully; no internal bypass (no abnormal mid-line temperature)
Defrost verified: sensor, board timing, valve actuation, outdoor-fan control
Auxiliary / emergency heat strips energize on demand; sequencer staging verified
Outdoor coil clear of ice and debris; base-pan drain open
Defrost termination and ambient sensors checked; balance-point and lockout settings verified
Dual-fuel changeover to gas furnace at the correct outdoor setpoint (where applicable)
Economizer, dampers & thermostat
Item | Result (Pass / Fail / N/A) | Notes
Economizer damper travels full open to full closed; actuator and linkage free, no binding
Outdoor-, return-, and mixed-air sensors within tolerance against a reference thermometer
Changeover setpoint (dry-bulb or enthalpy) and minimum position verified per sequence
Damper seals intact; barometric relief or power exhaust operates with economizer
Outside-air intake and louvers clear; bird screen and rain hood intact
Thermostat mode, setpoints, and schedule confirmed with customer; staging and fan settings correct
Thermostat calibration checked; remote sensors reading accurately
Thermostat batteries replaced where applicable; control wiring and terminals secure
BAS or smart-controller alarms reviewed and cleared
Measurements
Item | Result (Pass / Fail / N/A) | Notes
Airflow:
Cooling supply / return delta-T (°F) · 16–22 typ.
Static pressure across coil & filter / total external (in.wc) · Blower table
Electrical:
Run capacitor (µF) · Rated ± tol.
Start capacitor (µF) · Rated ± tol.
Compressor running amps (A) · RLA
Condenser fan motor amps (A)
Indoor blower motor amps (A)
Supply voltage L1-L2 / L2-L3 / L1-L3 (V)
Voltage imbalance (%)
Control transformer secondary (VAC) · 24
Cooling season: refrigerant charge:
Indoor entering wet-bulb (°F)
Outdoor dry-bulb (°F)
Suction pressure / saturation temp (psi/°F)
Liquid (high-side) pressure / saturation temp (psi/°F)
Suction line temp / superheat (fixed orifice: target-superheat method) (°F) · 8–12 (TXV)
Liquid line temp / subcooling (°F) · Mfr. (8–12)
Heating season: gas furnace:
Gas manifold pressure (in.wc) · NG 3.5 / LP 10–11
Flame sensor signal (µA)
Flue-gas O₂ / CO₂ (%)
Stack temperature (°F)
Steady-state efficiency (%)
CO: ambient / flue / supply air (ppm) · Safe limits
Temperature rise (°F) · Nameplate
Heat pump: heating mode:
Heating supply / return delta-T (°F) · 15–25 typ.
Heating suction pressure / saturation temp (psi/°F)
Heating discharge pressure / saturation temp (psi/°F)
Heat strip amp draw (per strip) (A)
Results
Item | Result (Pass / Fail / N/A) | Notes
Overall result: Operating normally / Deficiencies noted / Repair required / Red-tagged / shut down for safety
Safety condition found (cracked heat exchanger, high CO, refrigerant leak, electrical hazard)
Action taken
Customer / rep. notified: name
Contact
Date notified
Refrigerant added / recovered: type
Weight (lb / oz)
EPA leak rate (if leak found)
Photos attached (count / ref. #)
Combustion printout / meter readings ref.
Next PM: Cooling / Heating
Next due date
Deficiencies
Item | Result (Pass / Fail / N/A) | Notes
Unit ID ¦ Component ¦ Description ¦ Reading vs. spec ¦ Safety ¦ Effic. ¦ Monitor
Recommended repairs & replacements
Item | Result (Pass / Fail / N/A) | Notes
Recommendation ¦ Priority ¦ Quote / WO ref.
Consumables installed
Item | Result (Pass / Fail / N/A) | Notes
Item (filter / belt) ¦ Size ¦ Qty
Technician signature & EPA cert #
Customer / authorized representative
General planned-maintenance starting point compiled from publicly available manufacturer and industry guidance; not a manufacturer procedure. Superheat, subcooling, gas pressure, temperature rise, capacitor tolerance, and amp-draw figures are commonly cited ranges only; confirm against the nameplate and manufacturer literature. Combustion, refrigerant, and gas work must be done by qualified personnel; EPA Section 608 certification is required to handle refrigerant. Any CO, gas-leak, or cracked-heat-exchanger finding requires immediate corrective action. Codes and adopted amendments vary; verify with your AHJ.