## Checklist
Fire Sprinkler Visual Inspection Checklist
Fire Protection · Checklist · Free template from forz.io
Company:
Date:
Technician:
System & site
Item | Result (Pass / Fail / N/A) | Notes
Customer / facility
Account #
Site address
Building
Area / floors served
System type: Wet pipe / Dry pipe / Preaction / Deluge
Riser / system ID
No. of risers
Valve room location
No. of sprinklers
Hazard classification
Predominant sprinkler type: Upright / Pendent / Sidewall / ESFR / Dry
Weather
Ambient temp (°F)
Frequency cycle covered: Weekly / Monthly / Quarterly / Semiannual / Annual
Antifreeze loops present: Yes / No
Inspector name
Certification / license #
AHJ
NFPA 25 edition adopted
Last inspection date
Prior report # / open deficiencies
Gauge readings
Item | Result (Pass / Fail / N/A) | Notes
Water-supply pressure (wet pipe system) (psi)
Water-supply pressure (dry / preaction system) (psi)
Air / nitrogen pressure (dry, preaction, deluge) (psi)
Quick-opening device (QOD) gauge (psi)
Air compressor run / cutoff band (psi)
Fire pump suction pressure (if applicable) (psi)
Fire pump system pressure (if applicable) (psi)
Valve room / enclosure temperature (°F)
Visual inspection items
Item | Result (Pass / Fail / N/A) | Notes
Dry pipe, preaction, and deluge air or nitrogen pressure gauges within normal range for the listed differential
Dry pipe and preaction water-supply pressure gauges read normal
Control valves not locked or electrically supervised: correct open position, sealed, accessible
Valve room or enclosure kept above freezing (around 40 °F / 4 °C commonly cited); daily checks in freezing weather if no low-temp alarm
Fire pump house heat, ventilation louvers, and lighting operational (where a fire pump serves the system)
Fire pump suction, discharge, and bypass valves open; suction tank full; gauges normal; no visible leaks
Abnormal gauge readings, leaks, frost, or damage recorded for immediate follow-up
Wet pipe water-supply pressure gauge reads normal supply pressure
All gauges in good condition, legible, free of damage or fogging
Locked or supervised control valves: correct open position, accessible, no external leaks or tampering
Control valve identification signs present, legible, and secure
Post indicator valves (PIV) show OPEN, target visible, wrench in place
Alarm valve and riser free of damage; trim and retard chamber valves in correct position
Dry pipe / preaction valve exterior free of damage; trim valves in correct position
Dry pipe valve intermediate chamber not leaking through the drip check
QOD gauge consistent with dry pipe valve system-side gauge; QOD control valve open
Air compressor and low-air alarm switch undamaged; connections secure; compressor holds listed run/cutoff band
Backflow preventer visible, undamaged, both shutoff valves open (where installed)
Waterflow alarm devices (vane, paddle, pressure switch) undamaged and securely mounted
Valve supervisory (tamper) switches undamaged and securely mounted
Fire department connection (FDC) visible, accessible, and identified by sign
FDC caps or plugs in place; gaskets present; swivels and threads clear; interior unobstructed
FDC check valve not leaking; ball-drip / drain valve in place and clear
FDC piping and couplings undamaged and clear of storage, vehicles, and landscaping
Hydraulic design nameplate attached at riser, legible, and matching the system
Pressure-reducing / pressure-control valves in correct position, not leaking, handwheel in place
Hose connections, hose, gaskets, and pressure-restricting devices in place (combined standpipe)
Valve enclosure and heat source rechecked before the heating season
Dry / preaction trim, drip checks, and low-point drains free of condensate before cold weather
Dry, preaction, deluge, and alarm check valve gauges consistent with the differential
Supervisory and waterflow signal wiring, conduit, and connections free of corrosion or damage
Waterflow devices and tamper switches due for semiannual functional test noted (scheduled separately)
PRVs serving hose connections in correct set position, no external leakage
Sprinklers (from floor level) free of leakage, corrosion, foreign material, paint, damage, and loading; orientation correct
Corroded, loaded, or wrong-type sprinklers flagged; heads beyond listed service life noted
Required clearance maintained from deflectors to storage, ductwork, and obstructions
Pipe and fittings free of damage, leakage, corrosion, misalignment, and external loads
Hangers, sway bracing, and seismic restraints in place, secure, and undamaged
Pipe identification, control, and general information signs at riser legible and secure
Spare sprinkler cabinet stocked with correct quantity and types, matching wrench, and current spares list
Building survey for changes in occupancy, use, or storage affecting the design (evaluation only)
Information sign for antifreeze, dry, preaction, deluge, or auxiliary features present and legible
Low-temperature alarms in valve enclosures inspected at start of heating season, undamaged
Antifreeze loop identified, mapped, and labeled at riser and fill point
Antifreeze sampled from top and bottom of each system and tested before freezing weather
Measured concentration within listed limits (record in readings or notes; confirm against listing and AHJ)
Listed premixed antifreeze confirmed where required; legacy non-listed solutions flagged for owner
Low-point and auxiliary (drum) drains on dry and preaction systems drained before freezing weather
Heat trace, enclosure heaters, and freeze protection on exposed piping and FDC operational
Exposed or unheated areas, attics, and loading docks checked for piping exposed to freezing
Periodic tests & inspections: schedule check
Item | Result (Pass / Fail / N/A) | Notes
Gauges replaced or tested against calibrated gauge
Internal inspection for obstructing material
Internal inspection: dry / preaction, alarm, and check valves
Main drain test
Waterflow / alarm tests
Dry pipe valve trip test (partial / full)
Deluge full trip test
FDC piping hydrostatic test
Standpipe flow / hydrostatic test
Results & deficiencies
Item | Result (Pass / Fail / N/A) | Notes
# ¦ Location ¦ Deficiency / impairment ¦ Severity (C/N/I) ¦ NFPA 25 ref. ¦ Corrective action / WO #
Overall result: Pass / Deficiencies noted / Critical deficiency / Impairment in effect
Photos attached (count / ref #)
Proposal / quote / WO ref #
Impairment procedures followed: System tagged / Owner notified / AHJ / monitoring notified / Fire watch in place
Owner / rep notified: name & contact
Date notified
Next inspection due (by cycle)
Inspector signature & cert #
Owner / authorized representative signature
Covers visual inspection only, not the tests and maintenance NFPA 25 also requires. Frequencies differ by system type, and some items carry separate test or replacement intervals. Verify scope, frequencies, sprinkler service life, and antifreeze limits against your AHJ, the adopted edition, and the specific listings. This form is a starting point and does not replace the standard or inspection, testing, and maintenance by qualified personnel.