## Form
Fire Alarm Inspection & Test Report
Fire Protection · Form · Free template from forz.io
Company:
Date:
Technician:
Site & system identification
Item | Result (Pass / Fail / N/A) | Notes
Property name
Building / suite covered
Street address
Owner / responsible party
On-site contact & phone
Technician name
NICET / state license #
Inspection type: Weekly / Monthly / Quarterly / Semiannual / Annual
NFPA 72 edition adopted
Local amendments
FACU manufacturer
FACU model
FACU location
Software / firmware rev.
System type: Addressable / Conventional / Hybrid
No. of zones / points
Supervising station
Station phone
Station account #
On site: Record of completion / As-built drawings / Prior reports
Device count & test summary
Item | Result (Pass / Fail / N/A) | Notes
Manual pull stations
Smoke detectors (spot type)
Heat detectors
Duct smoke detectors
Carbon monoxide detectors
Waterflow switches
Valve tamper / supervisory switches
Pressure, low-air, low-temp supervisory
Monitor / control modules
Audible appliances (horns, speakers)
Visible appliances (strobes)
Remote annunciators
Remote power supplies / NACs
Other
Power & battery readings
Item | Result (Pass / Fail / N/A) | Notes
Battery manufacture date (date)
Battery rating (Ah)
Charger float / charging voltage (VDC)
Charging current (A)
Terminal voltage under full alarm load (VDC)
Measured capacity, % of rating (replace at or below 80%) (%)
Standby + alarm duration confirmed per design (hr)
Inspection & test items
Item | Result (Pass / Fail / N/A) | Notes
Visual: panel normal, no alarm, trouble, or supervisory conditions active
Visual: enclosure clean, undamaged, securely mounted, door key present
Visual: field wiring landed on terminals, no loose or corroded connections
Visual: fuses, LEDs, and power-supply indicators in normal state
Functional: lamp / LED test illuminates all panel indicators
Functional: panel sounder operates on alarm and trouble
Functional: trouble annunciates when IDC, NAC, and SLC circuits are opened
Functional: ground-fault detection annunciates when a fault is introduced
Functional: each alarm input produces the correct output sequence (cause and effect)
Disconnect, disable, or trouble conditions silence and restore correctly
Event history reviewed; panel time and date set to current
Walk test or single-point test of each addressable point logged at panel
Visual: primary (AC) power connected, on a dedicated breaker, breaker labeled
Functional: primary power removed; system transfers to secondary and annunciates AC loss
Visual: batteries free of corrosion, leakage, swelling, or heat damage
Battery terminals clean and torqued; interconnect cabling intact
Battery within manufacturer's listed life (verify against adopted edition)
Charger float / charging voltage and current within listed range
Load test under full alarm load: terminal voltage holds above manufacturer end voltage
Engine-driven generator or alternate source tested where it is the secondary supply
Visual: every device in place, undamaged, unobstructed, within listed spacing
Manual pull stations operated; alarm and correct address at panel; reset
Spot smoke detectors tested with listed aerosol or test gas; alarm and location label correct
Smoke detector sensitivity within listed range (first year, then alternate years, or self-test)
Heat detectors: restorable types tested per manufacturer; non-restorable by mechanical or simulated means
Duct smoke detectors: sampling airflow and alarm verified; fan shutdown interface confirmed
Carbon monoxide detectors tested per manufacturer (where part of the fire alarm system)
Waterflow switches flow-tested at adopted edition's interval; alarm within retard period
Valve tamper / supervisory switches operated; supervisory signal at panel
Pressure, low-air, and low-temperature supervisory devices operated; signal received
Addressable monitor / control modules report correct address and state
Device location labels and point list match the as-built record
Visual: horns, strobes, speakers, and combo units in place, undamaged, correctly mounted
Visual: strobe lenses clean; candela markings match approved plans
Functional: every audible appliance sounds during the alarm test
Functional: every visual appliance flashes during the alarm test
Sound pressure level meets required dBA above ambient in occupiable areas
Strobe synchronization confirmed within field of view where required
Voice evacuation messages intelligible (STI-PA or qualitative) at representative locations
Microphone, paging zones, and prerecorded message priority verified (where installed)
Visible appliances in sleeping areas meet required candela (where applicable)
Elevator Phase I recall: primary and alternate recall on lobby / machine-room / hoistway detectors
Elevator shunt trip and machine-room / hoistway smoke interface operate before recall (where provided)
HVAC fan shutdown and smoke-control sequences operate on the designated input
Smoke and fire dampers actuate to the correct position on alarm
Magnetic door holders release; rated doors close and latch
Electrically locked egress doors unlock on alarm (where interfaced)
Suppression releasing / preaction solenoid signals verified without discharge
Each control relay changes state and returns to normal after test
Remote annunciator display and LEDs mirror panel status during test
Annunciator acknowledge, silence, and reset operate and are access-restricted as designed
Graphic or LCD annunciator zone labels match field locations
Remote power supplies / NACs and repeaters report normal and annunciate trouble
Printer or event recorder logs events legibly (where installed)
System placed on test with the supervising station before transmitting
Both communication paths operate on dual-path communicators (e.g., IP plus cellular)
Account number, premises address, and zone descriptions on file verified
Call list, emergency contacts, and runner / response instructions current
System restored from test; station logged normal restoration
Supervising station signal log
Item | Result (Pass / Fail / N/A) | Notes
Alarm
Supervisory
Trouble
Path 1 failure
Path 2 failure
Restoral
Deficiencies & impairments
Item | Result (Pass / Fail / N/A) | Notes
Device type ¦ Address ¦ Location ¦ Deficiency ¦ Critical ¦ Corrective action / priority
Devices left in bypass or disabled
Item | Result (Pass / Fail / N/A) | Notes
Device / address ¦ Location ¦ Reason ¦ Planned restoration
Results & sign-off
Item | Result (Pass / Fail / N/A) | Notes
Overall result: system operates as intended: Pass / Fail
Critical deficiencies: owner notified in writing: Yes / No / None found
System restored to full automatic; all zones and station normal: Yes / No
Corrective actions: Completed on site / Recommended (see table)
Owner / representative notified: name
Date notified
Next weekly / monthly due
Next quarterly due
Next semiannual due
Next annual due
Technician signature & license #
Owner / authorized agent signature
Requirements come from the NFPA 72 inspection and testing chapter; chapter, table, and section numbering vary by edition. Frequencies shown are commonly cited (for example semiannual waterflow testing in the 2025 edition, annual functional testing of most devices, alternate-year smoke sensitivity) but can differ in your jurisdiction. Verify scope, test methods, and frequencies with your AHJ and the adopted edition. This form is a starting point, not the standard, and does not replace inspection or testing by qualified personnel.